## Chiller
rated chilled water outlet temp. ['C] | rated chilled water inlet temp. ['C] | rated chilled water flow [m3/min] | rated condenser water flow [m3/min] | rated condenser water inlet temp. ['C] | rated condenser water flow [m3/min] | rated power [kW] | chilled water pressure loss coefficient [kPa/(m3/min)^2] | condenser water pressure loss coefficient [kPa/(m3/min)^2]
7 | 15 | 3.145 | 32 | 37 | 5.925 | 299.717 | 1 | 1.1
condenser water inlet temp.-load factor | 0.1 | 0.2 | 0.4 | 0.6 | 0.8 | 1
12 | 16.09 | 23.87 | 25.15 | 20.16 | 15 | 11.11
16 | 7.52 | 12.56 | 15.86 | 14.77 | 12.21 | 9.67
20 | 4.55 | 8.05 | 11.19 | 11.35 | 10.1 | 8.44
24 | 3.13 | 5.73 | 8.47 | 9.07 | 8.5 | 7.42
28 | 2.32 | 4.35 | 6.72 | 7.48 | 7.28 | 6.57
32 | 1.82 | 3.45 | 5.51 | 6.31 | 6.33 | 5.87

## AirSourceHeatPump
rated chilled water outlet temp. ['C] | rated chilled water inlet temp. ['C] | rated chilled water flow [m3/min] | rated power [kW] | chilled water pressure loss coefficient [kPa/(m3/min)^2]
7 | 12 | 0.215 | 12.8059 | 13.9
condenser water inlet temp.-load factor | 0.2 | 0.4 | 0.6 | 0.8 | 1
15 | 14.3487 | 14.1145 | 13.0017 | 12.0646 | 11.069
20 | 12.4746 | 12.3575 | 11.3033 | 10.4248 | 9.6049
25 | 10.8348 | 10.6005 | 9.722 | 9.0192 | 8.1407
30 | 9.312 | 9.0778 | 8.3164 | 7.6722 | 6.9694
35 | 7.965 | 7.7307 | 7.0279 | 6.5594 | 5.8566
40 | 6.7937 | 6.5009 | 5.9152 | 5.5052 | 5.0367